SCAFFOLDING WORK NEAR 
OVERHEAD ELECTRIC LINES
INFORMATION SHEET

## Overview

This Information Sheet provides advice on managing the risks of erecting, dismantling and using fixed scaffolding near overhead electric lines and associated electrical equipment with an operating voltage up to and including 33,000 volts.

Where the operating voltage of the overhead electric lines is above 33,000 volts you should consult the Electricity Supply Authority and comply with all special conditions imposed 
by them.

More information is in the:

General guide for working in the vicinity 
of overhead and underground electric lines and associated material for:

  - operating cranes and mobile plant

  - tree and vegetation management

  - agricultural work

  - working near low voltage overhead electric lines near structures

  - transporting high loads

General guide for scaffolds and scaffolding work, and

AS/NZS 4576:1995: Guidelines for scaffolding.

## What are the risks?

Contact with energised overhead electric lines by erecting, dismantling and using fixed scaffolding can cause death, electric shock or other injury to plant operators and workers. This can be caused directly or indirectly by electricity—a close approach to line conductors may allow a ‘flashover’ to occur. The risk of flashover increases as the line voltage increases.

## What do I need to do?

You must manage the risks associated with scaffolding work near energised overhead electric lines and associated electrical equipment by:

identifying potential hazards

consulting workers and asset owners e.g. the Electricity Supply Authority or the person with management or control of the electric line or premises, and

deciding what work zones and approach distances are required for safe operations.

When assessing the risks consider:

the location, height, arrangement and visibility of overhead electric lines and supporting structures e.g. poles, towers and stay wires

the voltage of electric lines and exposed energised parts and whether they are insulated or bare

possible sway or sag of the electric lines

the scaffold’s dimensions and operating characteristics including inherent stability

conductivity if the scaffolds are earthed

the minimum clearance distance from the closest part of the scaffold or plant being 
used to the electric lines

erecting and dismantling scaffolding

the type of work activities required and the frequency of work tasks

qualifications, competency, skill and experience of people doing the work, and

safe work practices and procedures 
e.g. a safety observer and ‘permit to work’.

## Approach distances

AS/NZS 4576:1995: Guidelines for scaffolding sets a 4 metre approach distance for metallic scaffolding used near overhead electric lines.

When planning scaffolding work you should use 
4 metres initially and then consider other factors that may require a greater approach distance including:

the proximity of overhead electric lines

the proximity and operating radius of vehicles, cranes and other moving plant

environmental conditions e.g. storm activity, wind strength and direction, heavy rain, ice, hail and lightning, and

entry and exit for workers, materials and plant.

The 4 metre or greater approach distance applies in any direction where metallic scaffold is erected, used or dismantled near overhead electric lines.

If there is a risk the 4 metre approach (see Figure 1) distance cannot be maintained you should contact the Electricity Supply Authority to determine a safe system of work for the erection, use and dismantling of the scaffolding.

Figure 1 Four metre approach distance for metallic scaffolding

Electric lines should always be treated as energised unless you have:

an access authority confirming the electric lines have been de-energised, or

another written document from the Electricity Supply Authority which allows people to work in the No Go Zone.

The presence, location, type and operating voltage of all overhead electric lines should be verified by a competent person, for example an electrical engineer.

## How do I control the risks?

The best way to eliminate the hazard is by preventing people, plant, equipment and materials from coming close enough to energised overhead electric lines for direct contact or ‘flashover’ to occur. Consider:

de-energising the electric line

isolating and earthing the line for the duration of the work

re-routing the electric line away from the scaffolding after consultation and agreement of the Electricity Supply Authority, or

replacing existing overhead electric lines with underground electric cables.

De-energising or moving electric lines should be arranged with the Electricity Supply Authority as soon as possible.

Where elimination is not reasonably practicable, minimise the risks by substituting the hazard or work practice with something safer, for example by:

using alternative plant that cannot enter an unsafe zone, or

using non-conductive tools.

Consider isolating the hazard from people by erecting a physical barrier on the scaffold to prevent a person, anything attached to the person or anything held by the person from entering the specified approach distance or:

Use engineering controls like:

substituting the scaffold with an elevated work platform, or

using an insulated fibreglass handle on a paint roller instead of a conductive aluminium extension handle when standing on scaffolding.

If a risk still remains use administrative controls like:

a safety observer to warn people before they enter the 4 metre approach distance

arranging for the Electricity Supply Authority to identify exposed energised low voltage conductors, up to and including 1000 volts and fitting them with approved visual indicators

making hazards more visible by using approved visual indicators e.g. tiger tails. 
In this situation:

- tiger tails should be installed for the full length of the scaffolding plus a minimum distance of 5 metres beyond each end of the scaffolding

- a competent person should visually inspect the tiger tails each day before starting scaffolding operations, and

- if the tiger tails have moved or have been damaged, the Electricity Supply Authority should be contacted so they are replaced 
or relocated in the correct position.

Consultation with the Electricity Supply Authority will confirm the owner of the electric line and costs associated with the installation and application of tiger tails.

Note: Tiger tails do not provide protection against mechanical interference or electrical hazards. Using tiger tails does not allow workers to enter the 4 metre approach distance.

Also consider the use of personal protective equipment (PPE) including:

electrically tested insulating gloves, rubber soled boots and safety helmets

rubber insulating mats or on an equipotential conductive mat for workers to stand on, and

dry clothes especially in wet or humid conditions.

A combination of the above controls can be used if a single control is not enough to minimise the risks.

## Extra control measures for electrical wires passing through a scaffold

Where low voltage electrical wires or equipment pass through a scaffold they should be:

de-energised for the duration of the work, or

fully enclosed to meet the Electricity Supply Authority’s requirements (see Figures 2 
and 3) using a non-conductive material 
e.g. moisture resistant flooring grade particleboard, dry timber, dry plywood 
or similar material or plastic piping approved by the Electricity Supply Authority.

Figure 2 Enclosure on internal side of the scaffold

Figure 3 Fully enclosed energised low voltage electric lines passing through a scaffold

## Erected scaffolding using a hoarding and enclosure for reduced safety clearances

A hoarding is containment sheeting fixed to the external face of a scaffold to form a physical barrier between workers and overhead electric lines and associated electrical equipment.

Figure 4 shows the horizontal safety distances (A) and vertical mechanical clearances (B) from electrical conductors required by Electricity Supply Authorities.

You should check the clearance distances before erecting any scaffolding near overhead electric lines. An electrical engineer can provide the safety clearance distances used to design the scaffolding and control the risks. Clearance distances must be maintained.

The following installation conditions apply:

gaps between fitted sheets of plywood do not exceed 3 mm

no exposed cut or drilled holes in the sheets of plywood

the scaffolder uses non-conductive means 
to attach the plywood to the scaffold and ensures the arrangement can withstand the wind load, and

signs should be attached to the safe side of the hoarding warning of the electrical hazard and that the hoarding must not be removed.

Ensure a competent person visually inspects the hoarding and the enclosure daily to ensure they are in a satisfactory condition and remain impenetrable.

Figure 4 Scaffolding with hoarding

## Safe work method statements (SWMS)

A SWMS is required for energised electrical work and high risk construction work carried out on or near energised electrical installations or services. A written SWMS should be based on a risk assessment. The SWMS and risk assessment should be available to workers on site for the duration of the work.

Information and examples of what can 
go wrong when approach distances are not maintained are in Case studies – Incidents and scenarios.

For further information see the Safe Work Australia website (www.swa.gov.au).